| Photometric Test Report |  |  |
| --- | --- | --- |
| Report Number: POTS/GJ13067 | Report Date: 15-02-2013 | Prepared By: G John |
| Test Laboratory: Photometric and Optical Testing Services, Cotswold Business Centre, 42 A P Ellis Road, Rissington Business Park, Upper Rissington, Gloucestershire, GL54 2QB |  |  |
| Company Registration Number: Registered in England & Wales No. OC352911 |  |  |
| Registered Address: Thistle Down Barn, Holcot Lane, Sywell, Northampton, NN6 0BG |  |  |

| Client Details |  |
| --- | --- |
| Company: Astro Lighting | Email: technical@astrolighting.co.uk |
| Address: Astro Lighting Limited, G2 River Way, Harlow CM20 2DP, Great Britain |  |

| Details of Product Tested |  |
| --- | --- |
| Manufacturer: Astro Lighting | Source Type: Domestic light |
| Model: GOYA 760 LED MATT NICKEL | Serial Number: 0875 |
| Lamp Type: LED |  |
| Power Supply Used: Uninterruptible AC power supply |  |
| Voltage(AC V) = 243.2 | Current (mA)= 102 |
| Power (Watts)= 10.29 | Power factor= 0.428 |

| Integrating Sphere Test |  |  |
| --- | --- | --- |
| Date of Test: 12-02-2013 |  | Ambient Temperature:25°C |
| Measurement Filename: 0875 GOYA LED MATT NICKEL |  |  |
| Instrument Used: Labsphere model CSLMS HALOGEN 4060 integrating sphere spectroradiometer |  |  |
| Integrating Sphere Size: 1m |  | Measurement Geometry (2 / 4): 2 |
| Sample Orientation: Horizontal |  | Auxiliary Correction Applied: YES |
| Comments: |  |  |
| Date of Last Calibration (Operating Hours): 08-11-2012 (02:36) |  | Spectral Flux Standard Lamp Used: SCL-1400 |
| Standard Lamp Serial Number: K75 |  | Traceable: to NIST standards |
| Calibration Certificate Number: DM-02008-001 |  | Calibration Certificate Date: 19th February 2010 |
| Calibration Lamp Uncertainty: ± 0.67% (k=2) |  |  |
| Results |  |  |
| Flux (lumens): 630.8 |  |  |
| CIE 1931 Chromaticity Cx: 0.4245 |  | CIE 1931 Chromaticity Cy: 0.3962 |
| CRI (%):71.6 |  | CCT (K): 3153 |

Figure 1: Spectral Irradiance

Figure 2: CIE 1931 diagram.

| Goniophotometer Test |  |  |  |
| --- | --- | --- | --- |
| Date of Test: 12-02-2013 |  | Ambient Temperature: 25°C |  |
| Measurement Filename: 0875 GOYA 760 LED MATT NICKEL |  |  |  |
| Instrument Used: Radiant Imaging NFMS0800 Goniometer with ProMetric PM-1200N-1 Imaging Photometer |  |  |  |
| Photometer Working Distance: 1.5 m |  | Measurement Geometry: Near-Field |  |
| Comments: |  |  |  |
| Reference Photometer Used: Specbos1201 |  | Reference Photometer Serial Number: 2911670 |  |
| Traceable: to NPL standards, UKAS Accredited |  | Calibration Certificate Number: 121104 |  |
| Calibration Certificate Date: 25th October 2011 |  | Sample Stabilisation Time (minutes):75 |  |
| Reference Photometer Calibration Uncertainty: ± 2.4% (k=2, 20-200 lux, CIE illuminant A source) |  |  |  |
| Scan Set Up |  |  |  |
| Direction | Range |  | Increment |
| Inclination Zone 1 | 0-90° |  | 3° |
| Azimuth | 0-360° |  | 10° |
| Results |  |  |  |
| Integrated Luminous Flux (lumens):630.8 | Peak Intensity (3° Spot, candelas): 247.5 |  | Efficacy (lumens/Watt): 61.3 |
| Beam Angle (50% of max intensity C0-180, degrees): 112.4 |  |  |  |
| Photometric Filename (IES LM-63-2002): 0875 GOYA 760 LED MATT NICKEL |  |  |  |
| IES File – Absolute or Relative Format? RELATIVE |  |  |  |
| Photometric Filename (EULUMDAT): 0875 GOYA 760 LED MATT NICKEL |  |  |  |
| EULUMDAT File – Absolute or Relative Format? RELATIVE |  |  |  |

Figure 3: Far-Field Luminous Intensity (C0-180, Cartesian Coordinates)

Figure 4: Far-Field Luminous Intensity (C0-180, C90-270, Polar Coordinates)

Figure 4. Illuminance cone diagram.

Table 1. UGR values

|  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 |
| 3 | 246.3 | 247.5 | 245.3 | 242.5 | 241.1 | 241.0 | 241.8 | 241.9 | 241.2 | 241.1 | 243.4 | 243.5 | 244.0 | 242.0 | 240.5 | 240.5 | 240.9 | 240.8 | 240.6 |
| 6 | 236.0 | 236.5 | 242.5 | 240.6 | 235.9 | 233.5 | 233.3 | 235.1 | 237.0 | 241.5 | 242.1 | 238.4 | 236.1 | 239.0 | 238.3 | 237.9 | 235.4 | 237.2 | 241.9 |
| 9 | 236.5 | 236.1 | 236.8 | 231.5 | 233.6 | 236.5 | 236.9 | 237.4 | 238.4 | 234.1 | 232.0 | 235.7 | 234.2 | 232.8 | 236.2 | 235.6 | 235.4 | 230.0 | 242.0 |
| 12 | 232.4 | 234.6 | 236.2 | 238.0 | 235.3 | 231.6 | 233.2 | 239.0 | 239.7 | 230.9 | 231.1 | 231.7 | 232.9 | 231.8 | 227.9 | 237.6 | 234.3 | 228.8 | 243.2 |
| 15 | 226.0 | 237.2 | 229.8 | 225.4 | 228.7 | 232.2 | 234.8 | 228.2 | 232.7 | 230.1 | 228.5 | 228.9 | 228.3 | 228.9 | 227.6 | 232.2 | 237.6 | 227.5 | 241.4 |
| 18 | 224.0 | 229.2 | 230.4 | 230.4 | 227.6 | 223.9 | 226.8 | 227.1 | 227.7 | 224.3 | 227.2 | 225.0 | 220.8 | 229.5 | 222.9 | 223.2 | 229.6 | 218.4 | 232.5 |
| 21 | 227.8 | 222.4 | 224.0 | 223.0 | 217.2 | 221.7 | 217.5 | 216.5 | 219.3 | 217.8 | 220.4 | 218.7 | 220.4 | 217.3 | 228.0 | 208.7 | 229.6 | 212.2 | 230.8 |
| 24 | 217.6 | 220.8 | 216.7 | 220.2 | 222.3 | 211.1 | 222.7 | 212.8 | 211.3 | 216.6 | 213.8 | 221.2 | 215.4 | 210.0 | 216.7 | 209.4 | 218.1 | 203.0 | 222.9 |
| 27 | 217.7 | 214.9 | 214.0 | 210.4 | 212.2 | 212.1 | 208.1 | 211.0 | 204.3 | 205.2 | 208.7 | 206.5 | 205.6 | 207.2 | 203.3 | 204.0 | 206.4 | 201.4 | 212.6 |
| 30 | 207.3 | 209.1 | 201.0 | 203.0 | 201.6 | 202.0 | 203.5 | 200.7 | 202.3 | 201.9 | 197.1 | 199.6 | 200.6 | 202.9 | 201.0 | 197.2 | 204.7 | 188.9 | 201.4 |
| 33 | 204.0 | 195.0 | 197.5 | 190.0 | 198.3 | 192.2 | 196.9 | 197.8 | 191.7 | 193.6 | 190.9 | 196.9 | 188.0 | 197.8 | 186.5 | 194.6 | 193.6 | 189.7 | 203.8 |
| 36 | 191.0 | 189.4 | 185.4 | 187.2 | 181.8 | 189.5 | 180.6 | 188.0 | 184.2 | 185.3 | 186.3 | 182.6 | 183.6 | 180.3 | 176.9 | 189.1 | 182.5 | 182.7 | 195.9 |
| 39 | 184.9 | 179.8 | 174.7 | 179.4 | 181.4 | 173.7 | 175.5 | 171.4 | 174.5 | 175.5 | 177.1 | 175.1 | 175.0 | 174.8 | 166.8 | 175.9 | 165.1 | 167.9 | 184.9 |
| 42 | 173.7 | 166.2 | 174.8 | 175.3 | 164.1 | 166.8 | 170.6 | 166.2 | 169.1 | 167.7 | 163.7 | 166.2 | 166.3 | 161.4 | 163.9 | 170.0 | 161.4 | 163.8 | 173.6 |
| 45 | 167.6 | 156.3 | 153.8 | 165.8 | 160.8 | 153.2 | 158.3 | 159.1 | 157.5 | 157.3 | 154.5 | 158.5 | 156.7 | 150.8 | 153.2 | 156.0 | 144.5 | 154.3 | 164.7 |
| 48 | 151.1 | 149.9 | 154.3 | 142.1 | 148.2 | 149.8 | 144.8 | 147.4 | 146.3 | 149.7 | 145.6 | 148.9 | 143.1 | 141.7 | 147.5 | 147.0 | 134.0 | 145.3 | 152.9 |
| 51 | 137.3 | 137.1 | 142.0 | 134.5 | 130.9 | 129.5 | 140.1 | 134.9 | 135.9 | 133.6 | 133.9 | 133.7 | 131.0 | 132.8 | 136.2 | 136.2 | 124.0 | 135.6 | 145.4 |
| 54 | 130.3 | 121.7 | 127.6 | 125.3 | 127.5 | 127.8 | 127.7 | 123.3 | 121.4 | 125.0 | 123.1 | 121.3 | 120.1 | 120.3 | 125.1 | 123.1 | 111.0 | 124.6 | 131.8 |
| 57 | 119.9 | 108.3 | 111.5 | 113.4 | 116.6 | 112.1 | 113.6 | 113.4 | 110.6 | 110.4 | 112.4 | 109.1 | 107.4 | 110.5 | 107.7 | 106.0 | 99.9 | 110.7 | 120.0 |
| 60 | 108.5 | 101.6 | 104.7 | 93.7 | 101.7 | 102.8 | 98.0 | 98.2 | 92.6 | 94.1 | 91.1 | 93.3 | 98.4 | 97.7 | 99.6 | 98.7 | 92.7 | 98.8 | 107.0 |
| 63 | 90.6 | 86.2 | 93.6 | 89.8 | 86.2 | 82.2 | 79.1 | 74.1 | 70.7 | 63.8 | 65.6 | 68.5 | 78.1 | 85.8 | 90.2 | 82.4 | 81.0 | 83.7 | 91.6 |
| 66 | 78.7 | 75.2 | 78.7 | 77.6 | 72.6 | 65.3 | 54.5 | 43.6 | 40.7 | 35.2 | 34.0 | 39.1 | 54.5 | 68.5 | 73.4 | 72.8 | 71.0 | 75.8 | 81.1 |
| 69 | 70.4 | 63.3 | 65.7 | 64.2 | 59.5 | 44.0 | 29.0 | 17.9 | 17.1 | 10.6 | 9.1 | 13.5 | 23.7 | 43.5 | 54.2 | 57.3 | 60.7 | 69.8 | 68.7 |
| 72 | 56.9 | 55.7 | 52.8 | 48.6 | 32.4 | 13.1 | 6.1 | 3.0 | 3.0 | 3.0 | 1.0 | 2.6 | 6.5 | 19.0 | 34.4 | 48.4 | 50.0 | 52.7 | 55.9 |
| 75 | 44.2 | 45.8 | 38.5 | 30.4 | 10.6 | 1.5 | 0.0 | 0.7 | 0.5 | 0.8 | 0.8 | 0.0 | 0.0 | 1.7 | 12.1 | 32.2 | 38.8 | 44.4 | 43.3 |
| 78 | 32.9 | 31.7 | 28.3 | 8.7 | 0.3 | 0.9 | 0.0 | 1.0 | 0.4 | 0.6 | 0.5 | 0.6 | 0.6 | 0.3 | 0.0 | 9.2 | 26.9 | 32.1 | 32.2 |
| 81 | 21.0 | 21.6 | 9.2 | 1.7 | 0.0 | 0.0 | 0.0 | 0.0 | 0.5 | 0.2 | 0.4 | 0.3 | 0.0 | 0.0 | 0.6 | 0.0 | 9.7 | 20.9 | 22.2 |
| 84 | 11.6 | 6.9 | 1.0 | 0.6 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.6 | 8.7 | 11.3 |
| 87 | 3.5 | 0.5 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.6 | 2.3 | 4.4 |
| 90 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 1.2 |

Table 2a. Luminous intensity values, azimuth 0-180°

|  | 190 | 200 | 210 | 220 | 12 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 | 242.8 |
| 3 | 240.3 | 240.3 | 239.1 | 239.7 | 240.6 | 240.7 | 240.6 | 239.5 | 239.4 | 239.6 | 239.7 | 239.3 | 239.0 | 238.9 | 239.7 | 241.2 | 244.4 |
| 6 | 242.3 | 238.9 | 238.1 | 237.9 | 239.9 | 242.0 | 243.3 | 241.1 | 240.0 | 241.7 | 241.4 | 240.8 | 238.2 | 239.1 | 239.7 | 240.9 | 239.8 |
| 9 | 235.4 | 235.8 | 244.9 | 240.2 | 236.7 | 234.9 | 236.9 | 236.8 | 240.1 | 240.7 | 244.1 | 244.4 | 240.6 | 235.6 | 236.3 | 242.4 | 236.9 |
| 12 | 234.9 | 231.9 | 240.8 | 232.7 | 232.7 | 236.8 | 240.1 | 241.5 | 235.4 | 235.7 | 233.0 | 236.7 | 240.1 | 236.8 | 236.7 | 233.2 | 236.6 |
| 15 | 227.3 | 233.3 | 238.3 | 225.2 | 234.4 | 237.3 | 232.8 | 234.9 | 232.5 | 232.1 | 232.3 | 231.2 | 241.0 | 236.8 | 226.8 | 228.5 | 236.2 |
| 18 | 221.7 | 229.5 | 227.4 | 229.6 | 233.8 | 228.8 | 229.1 | 230.2 | 230.2 | 231.8 | 233.2 | 232.7 | 229.2 | 233.6 | 227.9 | 230.0 | 229.6 |
| 21 | 214.1 | 231.8 | 219.9 | 226.4 | 226.2 | 223.2 | 231.8 | 226.7 | 224.5 | 224.9 | 225.8 | 225.9 | 229.8 | 223.9 | 228.8 | 228.5 | 224.7 |
| 24 | 207.6 | 224.7 | 215.8 | 223.6 | 221.6 | 225.2 | 224.3 | 218.2 | 222.8 | 219.6 | 219.8 | 225.0 | 218.6 | 220.6 | 224.4 | 219.5 | 222.5 |
| 27 | 199.7 | 215.6 | 213.6 | 214.6 | 214.4 | 215.9 | 221.2 | 215.6 | 218.2 | 216.6 | 215.6 | 208.9 | 219.6 | 215.1 | 213.9 | 216.0 | 213.5 |
| 30 | 192.9 | 208.8 | 205.9 | 207.4 | 207.6 | 209.2 | 212.6 | 208.3 | 203.5 | 207.9 | 208.3 | 212.7 | 209.8 | 206.8 | 205.8 | 204.3 | 214.3 |
| 33 | 188.5 | 197.7 | 200.3 | 193.8 | 204.8 | 199.9 | 203.7 | 198.7 | 205.2 | 204.1 | 200.1 | 204.5 | 202.6 | 198.6 | 199.5 | 197.9 | 195.1 |
| 36 | 181.8 | 187.6 | 196.5 | 181.9 | 195.1 | 195.3 | 191.6 | 197.9 | 197.6 | 193.8 | 192.4 | 193.0 | 199.0 | 189.2 | 194.2 | 189.5 | 190.0 |
| 39 | 172.9 | 176.8 | 191.7 | 180.6 | 185.1 | 188.4 | 184.7 | 187.0 | 190.4 | 188.0 | 183.1 | 188.6 | 183.7 | 191.2 | 182.3 | 180.3 | 179.9 |
| 42 | 165.9 | 161.5 | 174.5 | 170.1 | 173.8 | 185.1 | 177.9 | 178.2 | 176.6 | 175.6 | 181.8 | 180.9 | 177.8 | 172.1 | 178.1 | 172.1 | 163.7 |
| 45 | 151.6 | 154.7 | 166.6 | 166.7 | 163.1 | 165.9 | 171.8 | 171.0 | 169.8 | 172.2 | 169.2 | 169.3 | 159.5 | 164.9 | 172.8 | 158.5 | 156.1 |
| 48 | 143.4 | 142.1 | 154.7 | 157.0 | 155.0 | 158.7 | 162.7 | 156.8 | 159.3 | 160.8 | 161.4 | 157.0 | 158.7 | 156.1 | 148.0 | 156.3 | 154.2 |
| 51 | 137.6 | 128.1 | 140.1 | 147.4 | 145.9 | 143.5 | 145.5 | 152.1 | 149.6 | 151.9 | 152.2 | 153.3 | 147.8 | 142.4 | 143.9 | 145.6 | 135.1 |
| 54 | 125.3 | 119.5 | 134.0 | 134.6 | 133.1 | 136.7 | 136.4 | 142.7 | 136.2 | 134.6 | 136.5 | 140.4 | 134.6 | 133.3 | 130.6 | 133.5 | 122.0 |
| 57 | 117.8 | 107.4 | 115.1 | 124.5 | 124.5 | 124.4 | 129.3 | 130.7 | 125.3 | 123.8 | 124.8 | 123.1 | 126.2 | 123.6 | 122.7 | 114.6 | 112.9 |
| 60 | 101.8 | 98.9 | 106.8 | 110.2 | 110.5 | 110.9 | 112.8 | 112.3 | 112.8 | 109.0 | 113.1 | 113.4 | 107.8 | 115.4 | 106.5 | 110.1 | 104.7 |
| 63 | 89.8 | 86.9 | 91.3 | 95.0 | 100.5 | 93.7 | 94.0 | 88.3 | 89.6 | 84.9 | 95.0 | 99.5 | 100.4 | 96.8 | 99.8 | 96.4 | 94.4 |
| 66 | 80.3 | 75.2 | 84.7 | 85.6 | 81.2 | 74.9 | 65.3 | 49.8 | 47.8 | 52.0 | 65.7 | 73.4 | 85.1 | 84.5 | 85.1 | 83.0 | 79.9 |
| 69 | 66.7 | 66.4 | 64.8 | 66.8 | 57.7 | 41.6 | 29.3 | 14.3 | 13.2 | 18.4 | 26.3 | 37.9 | 59.0 | 74.3 | 72.1 | 68.4 | 68.0 |
| 72 | 57.4 | 56.0 | 54.2 | 45.4 | 22.3 | 7.8 | 4.1 | 3.2 | 2.2 | 2.8 | 6.8 | 9.9 | 22.6 | 50.0 | 55.4 | 58.6 | 61.4 |
| 75 | 44.5 | 43.7 | 39.9 | 18.0 | 1.5 | 0.0 | 0.6 | 0.0 | 0.2 | 0.0 | 0.0 | 0.0 | 3.6 | 20.8 | 42.0 | 43.6 | 47.1 |
| 78 | 34.2 | 31.6 | 15.0 | 1.7 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 1.6 | 16.8 | 34.0 | 32.9 |
| 81 | 23.2 | 13.0 | 1.2 | 0.0 | 0.0 | 0.6 | 0.3 | 0.0 | 0.0 | 0.4 | 0.0 | 0.0 | 0.0 | 0.0 | 1.1 | 17.1 | 24.1 |
| 84 | 13.4 | 3.6 | 0.6 | 0.6 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.2 | 13.4 |
| 87 | 3.6 | 1.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.5 |
| 90 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |

Table 2b. Luminous intensity values, azimuth 190-350°

Signature:

_________________________________

Print Name:

GH JOHN

_________________________________

Date:

15-02-2013

_________________________________

Partner / Director
Duly authorised to sign on behalf of:

Photometric and Optical Testing Services LLP