| Photometric Test Report |  |  |
| --- | --- | --- |
| Report Number: POTS/GJ13103 | Report Date: 15-03-2013 | Prepared By: G John |
| Test Laboratory: Photometric and Optical Testing Services, Cotswold Business Centre, 42 A P Ellis Road, Rissington Business Park, Upper Rissington, Gloucestershire, GL54 2QB |  |  |
| Company Registration Number: Registered in England & Wales No. OC352911 |  |  |
| Registered Address: Thistle Down Barn, Holcot Lane, Sywell, Northampton, NN6 0BG |  |  |

| Client Details |  |
| --- | --- |
| Company: Astro Lighting | Email: technical@astrolighting.co.uk |
| Address: Astro Lighting Limited, G2 River Way, Harlow CM20 2DP, Great Britain |  |

| Details of Product Tested |  |
| --- | --- |
| Manufacturer: Astro Lighting | Source Type: Domestic light |
| Model: OSLO 100 | Serial Number: 7108 |
| Lamp Type: LED |  |
| Power Supply Used: Uninterruptible AC power supply |  |
| Voltage(AC V) = 246.2 | Current (mA)= 31 |
| Power (Watts)= 3.79 | Power factor= 0.500 |

| Integrating Sphere Test |  |  |
| --- | --- | --- |
| Date of Test: 06-03-2013 |  | Ambient Temperature:25°C |
| Measurement Filename: 7108 OSLO 100 |  |  |
| Instrument Used: Labsphere model CSLMS HALOGEN 4060 integrating sphere spectroradiometer |  |  |
| Integrating Sphere Size: 1m |  | Measurement Geometry (2 / 4): 4 |
| Sample Orientation: Horizontal |  | Auxiliary Correction Applied: YES |
| Comments: |  |  |
| Date of Last Calibration (Operating Hours): 08-11-2012 (02:36) |  | Spectral Flux Standard Lamp Used: SCL-1400 |
| Standard Lamp Serial Number: K75 |  | Traceable: to NIST standards |
| Calibration Certificate Number: DM-02008-001 |  | Calibration Certificate Date: 19th February 2010 |
| Calibration Lamp Uncertainty: ± 0.67% (k=2) |  |  |
| Results |  |  |
| Flux (lumens): 47.08 |  |  |
| CIE 1931 Chromaticity Cx: 0.4478 |  | CIE 1931 Chromaticity Cy: 0.4043 |
| CRI (%):85.05 |  | CCT (K): 2827 |

Figure 1: Spectral Irradiance

Figure 2: CIE 1931 diagram.

| Goniophotometer Test |  |  |  |
| --- | --- | --- | --- |
| Date of Test: 06-03-2013 |  | Ambient Temperature: 25°C |  |
| Measurement Filename: 7108 OSLO 100 |  |  |  |
| Instrument Used: Radiant Imaging NFMS0800 Goniometer with ProMetric PM-1200N-1 Imaging Photometer |  |  |  |
| Photometer Working Distance:2 m |  | Measurement Geometry: Near-Field |  |
| Comments: |  |  |  |
| Reference Photometer Used: Specbos1201 |  | Reference Photometer Serial Number: 2911670 |  |
| Traceable: to NPL standards, UKAS Accredited |  | Calibration Certificate Number: 121104 |  |
| Calibration Certificate Date: 25th October 2011 |  | Sample Stabilisation Time (minutes):24 |  |
| Reference Photometer Calibration Uncertainty: ± 2.4% (k=2, 20-200 lux, CIE illuminant A source) |  |  |  |
| Scan Set Up |  |  |  |
| Direction | Range |  | Increment |
| Inclination Zone 1 | 0-180° |  | 3° |
| Azimuth | 0-360° |  | 10° |
| Results |  |  |  |
| Integrated Luminous Flux (lumens):47.08 | Peak Intensity (3° Spot, candelas): 40.1 |  | Efficacy (lumens/Watt): 12.42 |
| Beam Angle (50% of max intensity C0-180, degrees): 50.2 |  |  |  |
| Photometric Filename (IES LM-63-2002): 7108 OSLO 100 |  |  |  |
| IES File – Absolute or Relative Format? Absolute |  |  |  |
| Photometric Filename (EULUMDAT): 7108 OSLO 100 |  |  |  |
| EULUMDAT File – Absolute or Relative Format? Absolute |  |  |  |

Figure 3: Far-Field Luminous Intensity (C0-180, Cartesian Coordinates)

Figure 4: Far-Field Luminous Intensity (C0-180, C90-270, Polar Coordinates)

Figure 4. Illuminance cone diagram.

Table 1. UGR values

|  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |
| 5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 10 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 20 | 0.5 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.3 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 25 | 0.9 | 0.7 | 0.6 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 30 | 1.5 | 1.2 | 0.8 | 0.6 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 35 | 1.8 | 1.5 | 1.1 | 0.7 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 40 | 2.1 | 1.7 | 1.3 | 0.8 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 45 | 2.2 | 1.9 | 1.3 | 0.8 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 50 | 2.4 | 1.9 | 1.3 | 0.8 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 55 | 2.7 | 2.1 | 1.4 | 0.7 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 60 | 4.2 | 3.2 | 1.4 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 65 | 18.7 | 12.9 | 2.4 | 0.8 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 70 | 35.4 | 31.4 | 6.9 | 0.8 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 75 | 38.1 | 36.6 | 9.2 | 0.7 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 80 | 38.5 | 37.0 | 7.1 | 0.7 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 85 | 38.4 | 37.2 | 6.4 | 0.5 | 0.2 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 90 | 38.3 | 36.9 | 7.4 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 95 | 37.9 | 36.7 | 7.9 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 100 | 37.6 | 36.6 | 8.5 | 0.6 | 0.2 | 0.2 | 0.3 | 0.3 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 105 | 37.9 | 36.1 | 7.4 | 0.6 | 0.4 | 0.3 | 0.6 | 0.3 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 110 | 37.8 | 33.5 | 8.5 | 1.0 | 1.0 | 1.2 | 1.3 | 0.5 | 0.2 | 0.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 115 | 26.6 | 17.6 | 4.1 | 2.5 | 2.6 | 2.2 | 2.5 | 1.4 | 1.0 | 0.7 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 120 | 6.8 | 7.6 | 5.8 | 5.1 | 4.5 | 3.6 | 3.4 | 2.5 | 1.9 | 1.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 125 | 8.7 | 7.0 | 6.6 | 5.9 | 5.5 | 4.8 | 4.5 | 4.2 | 3.7 | 2.3 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 130 | 9.2 | 8.3 | 7.7 | 7.2 | 6.6 | 5.9 | 5.4 | 5.5 | 5.4 | 3.3 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 135 | 9.7 | 9.1 | 8.4 | 7.6 | 7.1 | 6.6 | 6.6 | 6.3 | 6.2 | 3.9 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 140 | 9.6 | 9.0 | 8.4 | 7.7 | 7.2 | 6.8 | 6.7 | 6.8 | 6.9 | 4.4 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 145 | 9.2 | 8.7 | 8.1 | 7.6 | 7.2 | 6.9 | 7.0 | 6.8 | 6.8 | 4.3 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 150 | 8.5 | 8.3 | 7.8 | 7.3 | 7.0 | 6.8 | 7.0 | 6.7 | 6.4 | 4.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 155 | 7.7 | 7.6 | 7.4 | 7.1 | 6.9 | 6.8 | 6.7 | 6.6 | 5.7 | 4.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 160 | 7.0 | 7.0 | 6.9 | 6.8 | 6.6 | 6.6 | 6.6 | 6.2 | 5.0 | 3.9 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 165 | 7.0 | 6.8 | 6.7 | 6.6 | 6.6 | 6.5 | 6.1 | 5.4 | 4.6 | 4.2 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 170 | 6.9 | 6.9 | 6.8 | 6.7 | 6.3 | 5.9 | 5.3 | 4.6 | 4.4 | 4.4 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 175 | 6.0 | 5.9 | 5.7 | 5.5 | 5.2 | 4.9 | 4.7 | 4.5 | 4.3 | 4.1 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 |
| 180 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 |

Table 2a. Luminous intensity values, azimuth 0-180°

|  | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |
| 5 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |
| 10 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 |
| 15 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 |
| 20 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 |
| 25 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.7 | 0.8 | 0.9 |
| 30 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 1.1 | 1.4 | 1.5 |
| 35 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.2 | 0.3 | 0.5 | 1.0 | 1.6 | 1.9 | 2.0 |
| 40 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.2 | 0.2 | 0.3 | 0.6 | 1.3 | 2.0 | 2.2 | 2.2 |
| 45 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.2 | 0.3 | 0.8 | 1.6 | 2.2 | 2.5 | 2.4 |
| 50 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.2 | 0.3 | 0.9 | 1.9 | 2.3 | 2.6 | 2.6 |
| 55 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.2 | 0.3 | 1.0 | 2.0 | 2.8 | 3.0 | 2.9 |
| 60 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.2 | 0.4 | 1.1 | 2.4 | 5.0 | 6.4 | 6.4 |
| 65 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.3 | 0.5 | 1.6 | 3.9 | 9.3 | 13.0 | 13.0 |
| 70 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.3 | 0.7 | 2.2 | 6.1 | 21.2 | 31.5 | 36.3 |
| 75 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.4 | 0.8 | 3.0 | 9.2 | 35.2 | 38.3 | 39.1 |
| 80 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.3 | 0.4 | 0.9 | 4.8 | 13.3 | 36.3 | 39.5 | 39.8 |
| 85 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 | 0.2 | 0.8 | 1.4 | 6.0 | 19.6 | 37.3 | 39.8 | 40.1 |
| 90 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.2 | 1.2 | 2.0 | 5.3 | 29.4 | 37.2 | 39.4 | 39.8 |
| 95 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.5 | 1.1 | 2.2 | 3.3 | 7.7 | 25.1 | 36.9 | 38.5 | 38.4 |
| 100 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 1.1 | 2.0 | 3.3 | 4.5 | 8.6 | 19.5 | 36.9 | 38.5 | 38.1 |
| 105 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 2.1 | 3.8 | 4.7 | 5.4 | 6.8 | 12.7 | 35.0 | 38.8 | 39.9 |
| 110 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 3.1 | 5.5 | 6.0 | 6.3 | 7.5 | 11.9 | 29.1 | 35.7 | 38.6 |
| 115 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 3.7 | 6.3 | 6.7 | 7.2 | 8.3 | 10.3 | 16.4 | 20.2 | 18.9 |
| 120 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.3 | 7.0 | 7.2 | 7.3 | 8.2 | 9.5 | 10.2 | 11.0 | 10.6 |
| 125 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.3 | 7.0 | 7.1 | 7.4 | 8.0 | 9.3 | 9.8 | 10.3 | 10.1 |
| 130 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.3 | 7.0 | 7.0 | 7.3 | 7.9 | 9.0 | 9.6 | 9.8 | 9.8 |
| 135 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.1 | 6.8 | 6.9 | 7.3 | 7.6 | 9.0 | 9.5 | 9.7 | 9.7 |
| 140 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 3.9 | 6.7 | 6.8 | 7.1 | 7.6 | 8.4 | 9.4 | 9.7 | 9.7 |
| 145 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 3.9 | 6.6 | 6.8 | 7.0 | 7.2 | 8.0 | 8.7 | 9.3 | 9.4 |
| 150 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 3.8 | 6.2 | 6.7 | 6.9 | 7.2 | 7.6 | 8.1 | 8.5 | 8.6 |
| 155 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.0 | 5.7 | 6.6 | 6.7 | 7.1 | 7.3 | 7.5 | 7.7 | 7.8 |
| 160 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.2 | 5.3 | 6.3 | 6.5 | 6.7 | 7.0 | 7.0 | 7.1 | 7.1 |
| 165 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.0 | 4.9 | 5.7 | 6.2 | 6.4 | 6.6 | 6.8 | 6.9 | 7.0 |
| 170 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 3.9 | 4.5 | 5.1 | 5.6 | 6.1 | 6.3 | 6.6 | 6.8 | 6.8 |
| 175 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 3.9 | 4.2 | 4.6 | 4.9 | 5.2 | 5.4 | 5.6 | 5.8 | 5.9 |
| 180 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 | 2.0 |

Table 2b. Luminous intensity values, azimuth 190-350°

Signature:

_________________________________

Print Name:

GH JOHN

_________________________________

Date:

15-03-2013_________________________________

Partner / Director
Duly authorised to sign on behalf of:

Photometric and Optical Testing Services LLP