| Photometric Test Report |  |  |
| --- | --- | --- |
| Report Number: POTS/GJ13275 | Report Date: 25-07-2013 | Prepared By: G John |
| Test Laboratory: Photometric and Optical Testing Services, Cotswold Business Centre, 42 A P Ellis Road, Rissington Business Park, Upper Rissington, Gloucestershire, GL54 2QB |  |  |
| Company Registration Number: Registered in England & Wales No. OC352911 |  |  |
| Registered Address: Thistle Down Barn, Holcot Lane, Sywell, Northampton, NN6 0BG |  |  |

| Client Details |  |
| --- | --- |
| Company: Astro Lighting | Email: technical@astrolighting.co.uk |
| Address: Astro Lighting Limited, G2 River Way, Harlow CM20 2DP, Great Britain |  |

| Details of Product Tested |  |
| --- | --- |
| Manufacturer: Astro Lighting | Source Type: Domestic light |
| Model: BELGRAVIA LED 500 | Serial Number: 7133 |
| Lamp Type: LED |  |
| Power Supply Used: Uninterruptible AC power supply |  |
| Voltage(AC V) = 244.9 | Current (mA)= 76 |
| Power (Watts)= 15.63 | Power factor= 0.844 |

| Integrating Sphere Test |  |  |
| --- | --- | --- |
| Date of Test: 19-07-2013 |  | Ambient Temperature:25°C |
| Measurement Filename: 7133 BELGRAVIA LED 500 |  |  |
| Instrument Used: Labsphere model CSLMS HALOGEN 4060 integrating sphere spectroradiometer |  |  |
| Integrating Sphere Size: 1m |  | Measurement Geometry (2 / 4): 4 |
| Sample Orientation: Horizontal |  | Auxiliary Correction Applied: YES |
| Comments: |  |  |
| Date of Last Calibration (Operating Hours): 02-05-2013 (02:42) |  | Spectral Flux Standard Lamp Used: SCL-1400 |
| Standard Lamp Serial Number: K75 |  | Traceable: to NIST standards |
| Calibration Certificate Number: DM-02008-001 |  | Calibration Certificate Date: 19th February 2010 |
| Calibration Lamp Uncertainty: ± 0.67% (k=2) |  |  |
| Results |  |  |
| Flux (lumens):877.0 |  |  |
| CIE 1931 Chromaticity Cx: 0.3552 |  | CIE 1931 Chromaticity Cy: 0.3173 |
| CRI (%):81.51 |  | CCT (K): 4380 |

Figure 1: Spectral Irradiance

Figure 2: CIE 1931 diagram.

| Goniophotometer Test |  |  |  |
| --- | --- | --- | --- |
| Date of Test: 24-07-2013 |  | Ambient Temperature: 25°C |  |
| Measurement Filename: 7133 BELGRAVIA LED 500 |  |  |  |
| Instrument Used: Radiant Imaging NFMS0800 Goniometer with ProMetric PM-1200N-1 Imaging Photometer |  |  |  |
| Photometer Working Distance:1.5 m |  | Measurement Geometry: Near-Field |  |
| Comments: |  |  |  |
| Reference Photometer Used: Specbos1201 |  | Reference Photometer Serial Number: 2911670 |  |
| Traceable: to NPL standards, UKAS Accredited |  | Calibration Certificate Number: 13201 |  |
| Calibration Certificate Date: 15th March 2013 |  | Sample Stabilisation Time (minutes):60 |  |
| Reference Photometer Calibration Uncertainty: ± 2.4% (k=2, 20-200 lux, CIE illuminant A source) |  |  |  |
| Scan Set Up |  |  |  |
| Direction | Range |  | Increment |
| Inclination Zone 1 | 0-180° |  | 5° |
| Azimuth | 0-360° |  | 10° |
| Results |  |  |  |
| Integrated Luminous Flux (lumens):877.0 | Peak Intensity (3° Spot, candelas): 168.2 |  | Efficacy (lumens/Watt): 56.04 |
| Beam Angle (50% of max intensity C0-180, degrees): 112.5 |  |  |  |
| Photometric Filename (IES LM-63-2002): 7133 BELGRAVIA LED 500 |  |  |  |
| IES File – Absolute or Relative Format? Absolute |  |  |  |
| Photometric Filename (EULUMDAT): 7133 BELGRAVIA LED 500 |  |  |  |
| EULUMDAT File – Absolute or Relative Format? Absolute |  |  |  |

Figure 3: Far-Field Luminous Intensity (C0-180, Cartesian Coordinates)

Figure 4: Far-Field Luminous Intensity (C0-180, C90-270, Polar Coordinates)

Figure 4. Illuminance cone diagram.

Reflectance of

Ceiling	0.7	0.7	0.5	0.5	0.3	0.7	0.7	0.5	0.5	0.3

Wall	0.5	0.3	0.5	0.3	0.3	0.5	0.3	0.5	0.3	0.3

Floor Cavity	0.2	0.2	0.2	0.2	0.2	0.2	0.2	0.2	0.2	0.2

Room dimension	View endwise (C0)			View crosswise (C90)

x	y

2H	2H	13.0	14.3	13.6	15.0	15.8	17.4	18.7	18.0	19.4	20.1

3H	14.0	15.2	14.7	15.9	16.7	20.1	21.3	20.7	22.0	22.8

4H	14.3	15.5	15.0	16.2	17.0	21.5	22.7	22.2	23.4	24.2

6H	14.5	15.6	15.1	16.3	17.1	23.1	24.2	23.8	24.9	25.8

8H	14.4	15.5	15.1	16.2	17.1	23.9	25.0	24.6	25.7	26.5

12H	14.4	15.4	15.1	16.1	17.0	24.7	25.7	25.4	26.4	27.3

4H	2H	14.4	15.6	15.1	16.3	17.1	17.7	18.9	18.4	19.6	20.4

3H	15.7	16.8	16.4	17.5	18.3	20.6	21.7	21.3	22.4	23.2

4H	16.3	17.2	17.0	17.9	18.8	22.3	23.2	23.0	24.0	24.8

6H	16.5	17.4	17.2	18.1	19.0	24.0	24.9	24.7	25.6	26.5

8H	16.6	17.4	17.3	18.1	19.0	24.9	25.7	25.7	26.5	27.4

12H	16.6	17.3	17.3	18.1	19.0	25.9	26.6	26.6	27.4	28.3

8H	4H	17.4	18.2	18.1	19.0	19.8	22.4	23.2	23.2	24.0	24.9

6H	18.0	18.6	18.7	19.4	20.3	24.3	25.0	25.0	25.8	26.7

8H	18.2	18.8	19.0	19.6	20.5	25.4	26.0	26.2	26.8	27.7

12H	18.3	18.9	19.1	19.7	20.6	26.5	27.1	27.3	27.9	28.8

12H	4H	17.8	18.5	18.5	19.3	20.2	22.4	23.2	23.2	23.9	24.8

6H	18.6	19.2	19.3	20.0	20.9	24.4	25.0	25.2	25.8	26.7

8H	18.9	19.4	19.7	20.2	21.1	25.5	26.0	26.2	26.8	27.7

Table 1. UGR values

|  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 |
| 5 | 153 | 155 | 158 | 161 | 162 | 163 | 164 | 164 | 164 | 164 | 164 | 163 | 163 | 162 | 162 | 161 | 159 | 158 | 157 |
| 10 | 148 | 157 | 163 | 164 | 165 | 166 | 166 | 166 | 166 | 166 | 165 | 165 | 164 | 163 | 162 | 161 | 161 | 159 | 156 |
| 15 | 145 | 156 | 159 | 161 | 163 | 164 | 164 | 164 | 166 | 168 | 167 | 166 | 163 | 161 | 160 | 158 | 157 | 155 | 149 |
| 20 | 141 | 152 | 153 | 157 | 158 | 158 | 162 | 164 | 166 | 168 | 165 | 163 | 163 | 161 | 159 | 156 | 154 | 151 | 142 |
| 25 | 134 | 145 | 146 | 150 | 154 | 157 | 159 | 160 | 162 | 164 | 162 | 161 | 159 | 156 | 152 | 154 | 147 | 144 | 134 |
| 30 | 126 | 137 | 138 | 144 | 147 | 151 | 157 | 160 | 160 | 160 | 159 | 159 | 156 | 152 | 148 | 143 | 139 | 137 | 127 |
| 35 | 117 | 128 | 133 | 136 | 143 | 149 | 153 | 155 | 157 | 159 | 157 | 154 | 152 | 146 | 142 | 136 | 130 | 128 | 123 |
| 40 | 108 | 120 | 125 | 126 | 137 | 141 | 148 | 151 | 152 | 155 | 153 | 149 | 145 | 139 | 131 | 127 | 120 | 117 | 119 |
| 45 | 96 | 109 | 115 | 120 | 126 | 137 | 143 | 148 | 151 | 153 | 148 | 144 | 141 | 132 | 124 | 117 | 111 | 106 | 105 |
| 50 | 85 | 98 | 104 | 110 | 118 | 129 | 138 | 143 | 146 | 146 | 144 | 144 | 136 | 128 | 114 | 107 | 101 | 95 | 92 |
| 55 | 73 | 87 | 93 | 100 | 110 | 122 | 131 | 136 | 140 | 141 | 138 | 136 | 128 | 119 | 107 | 98 | 90 | 82 | 79 |
| 60 | 62 | 75 | 81 | 89 | 101 | 114 | 123 | 132 | 132 | 132 | 134 | 128 | 120 | 111 | 100 | 87 | 80 | 69 | 66 |
| 65 | 49 | 62 | 70 | 80 | 93 | 106 | 118 | 124 | 127 | 127 | 127 | 122 | 113 | 103 | 93 | 78 | 68 | 56 | 53 |
| 70 | 36 | 49 | 61 | 72 | 84 | 97 | 111 | 117 | 120 | 121 | 119 | 116 | 106 | 95 | 82 | 70 | 55 | 43 | 40 |
| 75 | 24 | 36 | 51 | 63 | 75 | 86 | 103 | 111 | 116 | 116 | 112 | 108 | 99 | 88 | 72 | 61 | 45 | 32 | 27 |
| 80 | 11 | 24 | 41 | 55 | 69 | 80 | 92 | 105 | 108 | 110 | 107 | 99 | 93 | 80 | 66 | 52 | 34 | 20 | 14 |
| 85 | 6 | 17 | 33 | 48 | 63 | 75 | 86 | 95 | 101 | 103 | 100 | 94 | 84 | 73 | 61 | 46 | 29 | 14 | 7 |
| 90 | 0 | 10 | 26 | 42 | 57 | 70 | 84 | 90 | 93 | 95 | 91 | 88 | 77 | 69 | 56 | 42 | 25 | 8 | 0 |
| 95 | 0 | 7 | 22 | 37 | 50 | 63 | 72 | 80 | 86 | 87 | 84 | 80 | 71 | 59 | 48 | 35 | 20 | 7 | 0 |
| 100 | 0 | 5 | 17 | 32 | 44 | 55 | 63 | 73 | 80 | 78 | 76 | 72 | 63 | 52 | 42 | 29 | 15 | 5 | 0 |
| 105 | 0 | 4 | 15 | 28 | 38 | 48 | 60 | 65 | 70 | 70 | 71 | 66 | 59 | 47 | 37 | 26 | 14 | 4 | 0 |
| 110 | 1 | 3 | 12 | 24 | 33 | 43 | 53 | 59 | 62 | 64 | 63 | 58 | 51 | 43 | 34 | 23 | 12 | 3 | 0 |
| 115 | 0 | 3 | 10 | 21 | 28 | 39 | 48 | 53 | 54 | 56 | 55 | 52 | 45 | 38 | 31 | 20 | 10 | 3 | 0 |
| 120 | 0 | 3 | 9 | 18 | 26 | 33 | 41 | 47 | 49 | 51 | 49 | 45 | 41 | 34 | 26 | 17 | 9 | 3 | 0 |
| 125 | 0 | 3 | 8 | 15 | 22 | 29 | 36 | 40 | 44 | 43 | 44 | 40 | 35 | 29 | 22 | 14 | 8 | 3 | 0 |
| 130 | 0 | 3 | 7 | 13 | 19 | 26 | 31 | 35 | 38 | 38 | 36 | 35 | 30 | 25 | 20 | 13 | 7 | 3 | 0 |
| 135 | 0 | 2 | 6 | 11 | 17 | 21 | 26 | 30 | 31 | 31 | 32 | 29 | 26 | 22 | 16 | 11 | 6 | 2 | 0 |
| 140 | 0 | 2 | 5 | 9 | 13 | 18 | 22 | 25 | 26 | 27 | 27 | 25 | 22 | 19 | 13 | 9 | 5 | 2 | 0 |
| 145 | 0 | 2 | 4 | 8 | 11 | 15 | 18 | 20 | 22 | 23 | 22 | 20 | 18 | 15 | 11 | 8 | 4 | 2 | 0 |
| 150 | 0 | 2 | 4 | 7 | 9 | 13 | 15 | 16 | 17 | 18 | 18 | 17 | 15 | 12 | 9 | 7 | 4 | 2 | 0 |
| 155 | 0 | 2 | 3 | 5 | 8 | 10 | 11 | 12 | 14 | 14 | 14 | 12 | 11 | 9 | 7 | 6 | 3 | 2 | 1 |
| 160 | 0 | 2 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 10 | 10 | 9 | 8 | 7 | 6 | 4 | 3 | 1 | 1 |
| 165 | 0 | 2 | 2 | 3 | 4 | 5 | 6 | 6 | 7 | 7 | 7 | 6 | 6 | 5 | 4 | 3 | 2 | 1 | 1 |
| 170 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 1 | 1 |
| 175 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 |
| 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Table 2a. Luminous intensity values, azimuth 0-180°

|  | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 |
| 5 | 158 | 160 | 161 | 162 | 163 | 164 | 164 | 164 | 164 | 164 | 163 | 163 | 162 | 162 | 160 | 158 | 155 |
| 10 | 160 | 163 | 164 | 165 | 166 | 166 | 166 | 166 | 166 | 165 | 165 | 164 | 163 | 162 | 161 | 161 | 156 |
| 15 | 157 | 159 | 161 | 163 | 164 | 164 | 164 | 166 | 168 | 167 | 166 | 163 | 161 | 160 | 158 | 157 | 154 |
| 20 | 152 | 153 | 157 | 158 | 158 | 162 | 164 | 166 | 168 | 165 | 163 | 163 | 161 | 159 | 156 | 154 | 151 |
| 25 | 145 | 146 | 150 | 154 | 157 | 159 | 160 | 162 | 164 | 162 | 161 | 159 | 156 | 152 | 154 | 147 | 144 |
| 30 | 137 | 138 | 144 | 147 | 151 | 157 | 160 | 160 | 160 | 159 | 159 | 156 | 152 | 148 | 143 | 139 | 137 |
| 35 | 128 | 133 | 136 | 143 | 149 | 153 | 155 | 157 | 159 | 157 | 154 | 152 | 146 | 142 | 136 | 130 | 128 |
| 40 | 120 | 125 | 126 | 137 | 141 | 148 | 151 | 152 | 155 | 153 | 149 | 145 | 139 | 131 | 127 | 120 | 117 |
| 45 | 109 | 115 | 120 | 126 | 137 | 143 | 148 | 151 | 153 | 148 | 144 | 141 | 132 | 124 | 117 | 111 | 106 |
| 50 | 98 | 104 | 110 | 118 | 129 | 138 | 143 | 146 | 146 | 144 | 144 | 136 | 128 | 114 | 107 | 101 | 95 |
| 55 | 87 | 93 | 100 | 110 | 122 | 131 | 136 | 140 | 141 | 138 | 136 | 128 | 119 | 107 | 98 | 90 | 82 |
| 60 | 75 | 81 | 89 | 101 | 114 | 123 | 132 | 132 | 132 | 134 | 128 | 120 | 111 | 100 | 87 | 80 | 69 |
| 65 | 62 | 70 | 80 | 93 | 106 | 118 | 124 | 127 | 127 | 127 | 122 | 113 | 103 | 93 | 78 | 68 | 56 |
| 70 | 49 | 61 | 72 | 84 | 97 | 111 | 117 | 120 | 121 | 119 | 116 | 106 | 95 | 82 | 70 | 55 | 43 |
| 75 | 36 | 51 | 63 | 75 | 86 | 103 | 111 | 116 | 116 | 112 | 108 | 99 | 88 | 72 | 61 | 45 | 32 |
| 80 | 24 | 41 | 55 | 69 | 80 | 92 | 105 | 108 | 110 | 107 | 99 | 93 | 80 | 66 | 52 | 34 | 20 |
| 85 | 17 | 33 | 48 | 63 | 75 | 86 | 95 | 101 | 103 | 100 | 94 | 84 | 73 | 61 | 46 | 29 | 14 |
| 90 | 10 | 26 | 42 | 57 | 70 | 84 | 90 | 93 | 95 | 91 | 88 | 77 | 69 | 56 | 42 | 25 | 8 |
| 95 | 7 | 22 | 37 | 50 | 63 | 72 | 80 | 86 | 87 | 84 | 80 | 71 | 59 | 48 | 35 | 20 | 7 |
| 100 | 5 | 17 | 32 | 44 | 55 | 63 | 73 | 80 | 78 | 76 | 72 | 63 | 52 | 42 | 29 | 15 | 5 |
| 105 | 4 | 15 | 28 | 38 | 48 | 60 | 65 | 70 | 70 | 71 | 66 | 59 | 47 | 37 | 26 | 14 | 4 |
| 110 | 3 | 12 | 24 | 33 | 43 | 53 | 59 | 62 | 64 | 63 | 58 | 51 | 43 | 34 | 23 | 12 | 3 |
| 115 | 3 | 10 | 21 | 28 | 39 | 48 | 53 | 54 | 56 | 55 | 52 | 45 | 38 | 31 | 20 | 10 | 3 |
| 120 | 3 | 9 | 18 | 26 | 33 | 41 | 47 | 49 | 51 | 49 | 45 | 41 | 34 | 26 | 17 | 9 | 3 |
| 125 | 3 | 8 | 15 | 22 | 29 | 36 | 40 | 44 | 43 | 44 | 40 | 35 | 29 | 22 | 14 | 8 | 3 |
| 130 | 3 | 7 | 13 | 19 | 26 | 31 | 35 | 38 | 38 | 36 | 35 | 30 | 25 | 20 | 13 | 7 | 3 |
| 135 | 2 | 6 | 11 | 17 | 21 | 26 | 30 | 31 | 31 | 32 | 29 | 26 | 22 | 16 | 11 | 6 | 2 |
| 140 | 2 | 5 | 9 | 13 | 18 | 22 | 25 | 26 | 27 | 27 | 25 | 22 | 19 | 13 | 9 | 5 | 2 |
| 145 | 2 | 4 | 8 | 11 | 15 | 18 | 20 | 22 | 23 | 22 | 20 | 18 | 15 | 11 | 8 | 4 | 2 |
| 150 | 2 | 4 | 7 | 9 | 13 | 15 | 16 | 17 | 18 | 18 | 17 | 15 | 12 | 9 | 7 | 4 | 2 |
| 155 | 2 | 3 | 5 | 8 | 10 | 11 | 12 | 14 | 14 | 14 | 12 | 11 | 9 | 7 | 6 | 3 | 2 |
| 160 | 2 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 10 | 10 | 9 | 8 | 7 | 6 | 4 | 3 | 1 |
| 165 | 2 | 2 | 3 | 4 | 5 | 6 | 6 | 7 | 7 | 7 | 6 | 6 | 5 | 4 | 3 | 2 | 1 |
| 170 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 1 |
| 175 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 |
| 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Table 2b. Luminous intensity values, azimuth 190-350°

Signature:

_________________________________

Print Name:

GH JOHN

_________________________________

Date:

__25-07-2013_______________________________

Partner / Director
Duly authorised to sign on behalf of:

Photometric and Optical Testing Services LLP