| Photometric Test Report |  |  |
| --- | --- | --- |
| Report Number: POTS/DC14287 | Report Date: 20/11/2014 | Prepared By: D CHAMBERS |
| Test Laboratory: Photometric and Optical Testing Services, Cheltenham Film and Photographic Studios, Hatherley Lane, Cheltenham, Gloucestershire, GL51 6PN |  |  |
| Company Registration Number: Registered in England & Wales No. OC352911 |  |  |
| Registered Address: Thistle Down Barn, Holcot Lane, Sywell, Northampton, NN6 0BG |  |  |

| Client Details |  |
| --- | --- |
| Company: Astro Lighting | Email: technical@astrolighting.co.uk |
| Address: Astro Lighting Limited, G2 River Way, Harlow CM20 2DP, Great Britain |  |

| Test Method(s) Used |  |
| --- | --- |
| POTS Standard Operating Procedure: | INTEGRATING SPHERE PROCEDURE POTS016 |
| POTS Standard Operating Procedure: | NFMS OPERATION GUIDE |
| Standard: | LM79 08 |

| Details of Product Tested |  |
| --- | --- |
| Manufacturer: ASTRO LIGHTING | Source Type: LED |
| Model: 7394 MASSA 350 | Luminaire Type: DOWNLIGHT |
| Power Supply Used: Kikusui PCR1000M Voltage Stabiliser S/N SM01191 |  |
| Voltage(AC V) = 230 | Current (mA)= 138 |
| Power (Watts)= 24.45 | Power factor= 0.770 |

| Integrating Sphere Test |  |  |
| --- | --- | --- |
| Date of Test: 18/1/2014 |  | Ambient Temperature:25°C |
| Measurement Filename: 7394 MASSA 350 |  |  |
| Instrument Used: Labsphere model 2m integrating sphere spectroradiometer AS-02949-012 |  |  |
| Integrating Sphere Size: 2m |  | Measurement Geometry (2 / 4): 4 |
| Sample Orientation: Horizontal |  | Auxiliary Correction Applied: YES |
| Comments: |  |  |
| Date of Last Calibration (Operating Hours): 28-10-2014 (0:15) |  | Spectral Flux Standard Lamp Used: SCL-600 |
| Standard Lamp Serial Number: L123 |  | Traceable: to NIST standards |
| Calibration Certificate Number: SCL-600-L123 |  | Calibration Certificate Date: 29/01/2014 |
| Calibration Lamp Uncertainty: ± 0.67% (k=2) |  |  |
| Results |  |  |
| Flux (lumens): 1367 |  |  |
| CIE 1931 Chromaticity Cx: 0.4389 |  | CIE 1931 Chromaticity Cy: 0.4024 |
| CRI (%):82.56 |  | CCT (K): 2953 |

Figure 1: Spectral Irradiance

Figure 2: CIE 1931 diagram.

| Goniophotometer Test |  |  |  |
| --- | --- | --- | --- |
| Date of Test: 18/11/2014 |  | Ambient Temperature: 25°C |  |
| Measurement Filename: 7394 MASSA 350 |  |  |  |
| Instrument Used: Radiant Imaging NFMS0800 Goniometer with ProMetric PM-1200N-1 Imaging Photometer |  |  |  |
| Photometer Working Distance: 4m |  | Measurement Geometry: Near-Field |  |
| Comments: |  |  |  |
| Reference Photometer Used: Specbos1211 |  | Reference Photometer Serial Number: 2014754 |  |
| Traceable: to NIST standards |  | Calibration Certificate Number: 2129 WK-L 2014-02 |  |
| Calibration Certificate Date: 13 February 2014 |  | Sample Stabilisation Time (minutes): 60 |  |
| Reference Photometer Calibration Uncertainty: ± 2.4% (k=2, 20-200 lux, CIE illuminant A source) |  |  |  |
| Scan Set Up |  |  |  |
| Direction | Range |  | Increment |
| Inclination Zone 1 | 0-180° |  | 3° |
| Azimuth | 0-360° |  | 10° |
| Results |  |  |  |
| Integrated Luminous Flux (lumens):1367 | Peak Intensity (3° Spot, candelas):397.4 |  | Efficacy (lumens/Watt): 55.9 |
| Beam Angle (50% of max intensity C0-180, degrees): 119.4 |  |  |  |
| Photometric Filename (IES LM-63-2002): 7394 MASSA 350 |  |  |  |
| IES File – Absolute or Relative Format? ABSOLUTE |  |  |  |
| Photometric Filename (EULUMDAT): 7394 MASSA 350 |  |  |  |
| EULUMDAT File – Absolute or Relative Format? ABSOLUTE |  |  |  |

Figure 3: Far-Field Luminous Intensity (C0-180, Cartesian Coordinates)

Figure 4: Far-Field Luminous Intensity (C0-180, C90-270, Polar Coordinates)

Figure 5. Cone diagram for mounting height of 6 metres.

Reflectance of

Ceiling	0.7	0.7	0.5	0.5	0.3	0.7	0.7	0.5	0.5	0.3

Wall	0.5	0.3	0.5	0.3	0.3	0.5	0.3	0.5	0.3	0.3

Floor Cavity	0.2	0.2	0.2	0.2	0.2	0.2	0.2	0.2	0.2	0.2

Room dimension	View endwise (C0)			View crosswise (C90)

x	y

2H	2H	14.0	15.6	14.4	16.0	16.5	14.1	15.7	14.5	16.1	16.6

3H	15.7	17.2	16.2	17.7	18.1	15.9	17.3	16.3	17.8	18.2

4H	16.6	18.0	17.1	18.4	18.9	16.7	18.1	17.2	18.6	19.1

6H	17.4	18.7	17.9	19.2	19.7	17.5	18.8	18.0	19.3	19.8

8H	17.8	19.0	18.3	19.5	20.1	17.9	19.1	18.4	19.6	20.1

12H	18.2	19.4	18.7	19.9	20.4	18.2	19.4	18.7	19.9	20.5

4H	2H	14.7	16.1	15.2	16.5	17.0	14.8	16.2	15.3	16.7	17.1

3H	16.6	17.8	17.1	18.3	18.9	16.7	18.0	17.2	18.4	19.0

4H	17.7	18.7	18.2	19.3	19.8	17.8	18.9	18.3	19.4	19.9

6H	18.6	19.6	19.2	20.1	20.7	18.7	19.7	19.3	20.2	20.8

8H	19.1	20.0	19.6	20.5	21.1	19.2	20.1	19.7	20.6	21.2

12H	19.6	20.4	20.1	21.0	21.6	19.6	20.5	20.2	21.0	21.6

8H	4H	18.0	18.9	18.6	19.5	20.1	18.2	19.1	18.7	19.6	20.2

6H	19.2	20.0	19.7	20.5	21.1	19.3	20.1	19.8	20.6	21.2

8H	19.8	20.5	20.4	21.1	21.7	19.9	20.6	20.5	21.2	21.8

12H	20.5	21.1	21.0	21.7	22.3	20.5	21.1	21.1	21.7	22.3

12H	4H	18.1	19.0	18.7	19.5	20.1	18.2	19.1	18.8	19.6	20.2

6H	19.4	20.0	19.9	20.6	21.2	19.4	20.1	20.0	20.7	21.3

8H	20.0	20.6	20.6	21.2	21.8	20.1	20.7	20.7	21.3	21.9

Distance between luminaires: 0.25

Due to missing symmetry characteristics the values apply only to the indicated line of sight.

Table 1. UGR values

|  | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 |
| 3 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 |
| 6 | 396 | 396 | 396 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 396 | 396 | 396 | 396 | 396 | 395 | 395 |
| 9 | 392 | 392 | 392 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 392 | 392 | 393 | 393 | 393 | 393 | 393 | 393 |
| 12 | 387 | 387 | 386 | 386 | 386 | 386 | 386 | 386 | 386 | 386 | 386 | 386 | 387 | 388 | 389 | 389 | 389 | 389 | 389 |
| 15 | 382 | 381 | 381 | 381 | 380 | 381 | 381 | 381 | 381 | 382 | 381 | 381 | 381 | 382 | 383 | 383 | 384 | 383 | 384 |
| 18 | 376 | 376 | 376 | 376 | 375 | 375 | 375 | 375 | 376 | 376 | 376 | 375 | 375 | 376 | 376 | 377 | 377 | 378 | 377 |
| 21 | 369 | 369 | 370 | 369 | 368 | 368 | 369 | 369 | 368 | 368 | 370 | 370 | 369 | 369 | 370 | 370 | 371 | 371 | 370 |
| 24 | 361 | 361 | 360 | 360 | 359 | 360 | 361 | 361 | 360 | 359 | 362 | 363 | 360 | 361 | 361 | 361 | 363 | 364 | 363 |
| 27 | 351 | 351 | 349 | 350 | 350 | 350 | 351 | 352 | 351 | 349 | 351 | 352 | 350 | 352 | 351 | 351 | 354 | 355 | 354 |
| 30 | 340 | 340 | 339 | 340 | 340 | 339 | 340 | 341 | 340 | 338 | 339 | 340 | 340 | 340 | 340 | 340 | 343 | 344 | 344 |
| 33 | 330 | 329 | 329 | 328 | 329 | 328 | 328 | 329 | 328 | 327 | 329 | 328 | 330 | 330 | 330 | 329 | 332 | 332 | 332 |
| 36 | 318 | 318 | 318 | 316 | 317 | 316 | 315 | 316 | 315 | 316 | 317 | 315 | 318 | 318 | 318 | 318 | 319 | 319 | 320 |
| 39 | 304 | 304 | 305 | 302 | 303 | 303 | 301 | 303 | 302 | 303 | 305 | 303 | 305 | 304 | 305 | 305 | 306 | 305 | 308 |
| 42 | 290 | 289 | 290 | 288 | 289 | 289 | 288 | 289 | 288 | 288 | 290 | 289 | 291 | 290 | 291 | 291 | 292 | 290 | 295 |
| 45 | 275 | 274 | 273 | 274 | 273 | 273 | 274 | 274 | 273 | 273 | 274 | 274 | 276 | 276 | 276 | 275 | 276 | 276 | 280 |
| 48 | 260 | 259 | 258 | 260 | 257 | 257 | 259 | 259 | 257 | 257 | 258 | 259 | 260 | 259 | 260 | 260 | 262 | 261 | 264 |
| 51 | 244 | 244 | 242 | 245 | 241 | 241 | 242 | 242 | 241 | 240 | 243 | 242 | 244 | 243 | 244 | 245 | 245 | 246 | 249 |
| 54 | 227 | 227 | 227 | 225 | 224 | 226 | 224 | 225 | 225 | 224 | 227 | 225 | 226 | 227 | 227 | 227 | 230 | 230 | 232 |
| 57 | 212 | 211 | 210 | 208 | 208 | 211 | 208 | 208 | 208 | 208 | 210 | 209 | 210 | 211 | 211 | 211 | 213 | 213 | 215 |
| 60 | 196 | 195 | 193 | 191 | 191 | 193 | 191 | 192 | 191 | 193 | 192 | 193 | 193 | 194 | 194 | 194 | 195 | 196 | 197 |
| 63 | 179 | 179 | 179 | 176 | 174 | 174 | 175 | 176 | 175 | 177 | 175 | 176 | 177 | 177 | 177 | 178 | 180 | 180 | 181 |
| 66 | 161 | 161 | 162 | 161 | 159 | 159 | 159 | 160 | 159 | 160 | 159 | 160 | 162 | 162 | 162 | 163 | 163 | 165 | 165 |
| 69 | 146 | 146 | 145 | 145 | 144 | 143 | 143 | 144 | 144 | 144 | 143 | 145 | 145 | 146 | 146 | 147 | 148 | 150 | 150 |
| 72 | 132 | 133 | 131 | 131 | 131 | 129 | 129 | 130 | 130 | 130 | 130 | 131 | 130 | 131 | 132 | 132 | 134 | 135 | 136 |
| 75 | 119 | 120 | 118 | 118 | 117 | 116 | 115 | 117 | 117 | 116 | 116 | 118 | 116 | 118 | 118 | 118 | 120 | 120 | 122 |
| 78 | 106 | 106 | 105 | 106 | 104 | 104 | 103 | 103 | 104 | 103 | 103 | 104 | 104 | 105 | 105 | 106 | 107 | 107 | 109 |
| 81 | 96 | 94 | 96 | 96 | 94 | 95 | 93 | 93 | 94 | 92 | 91 | 93 | 92 | 93 | 92 | 94 | 95 | 93 | 94 |
| 84 | 85 | 85 | 83 | 85 | 83 | 83 | 83 | 83 | 82 | 81 | 81 | 80 | 81 | 80 | 81 | 83 | 82 | 82 | 82 |
| 87 | 73 | 73 | 73 | 74 | 73 | 73 | 72 | 74 | 71 | 72 | 70 | 71 | 70 | 71 | 72 | 73 | 72 | 74 | 73 |
| 90 | 66 | 64 | 63 | 65 | 61 | 62 | 63 | 66 | 63 | 61 | 63 | 62 | 62 | 62 | 62 | 64 | 63 | 65 | 69 |
| 93 | 54 | 55 | 55 | 56 | 53 | 53 | 53 | 55 | 52 | 52 | 53 | 52 | 53 | 54 | 54 | 56 | 56 | 56 | 62 |
| 96 | 45 | 45 | 45 | 44 | 45 | 44 | 45 | 44 | 44 | 44 | 43 | 43 | 44 | 45 | 45 | 45 | 47 | 48 | 60 |
| 99 | 36 | 37 | 35 | 35 | 35 | 35 | 36 | 35 | 36 | 35 | 36 | 34 | 35 | 35 | 36 | 37 | 37 | 41 | 57 |
| 102 | 28 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 25 | 27 | 27 | 27 | 28 | 31 | 53 |
| 105 | 18 | 20 | 19 | 19 | 19 | 18 | 18 | 19 | 19 | 18 | 17 | 17 | 17 | 17 | 19 | 18 | 18 | 22 | 49 |
| 108 | 9 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 14 | 44 |
| 111 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 6 | 40 |
| 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 35 |
| 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 |
| 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 |
| 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 |
| 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |
| 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 |
| 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 |
| 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 |
| 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 |
| 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |
| 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |
| 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Table 2a. Luminous intensity values, azimuth 0-180°

|  | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 |
| 3 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 | 397 |
| 6 | 395 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 395 | 395 | 394 | 394 | 394 | 394 | 395 | 395 |
| 9 | 392 | 392 | 392 | 393 | 393 | 394 | 394 | 394 | 394 | 393 | 392 | 391 | 390 | 390 | 391 | 392 | 392 |
| 12 | 388 | 388 | 388 | 389 | 389 | 389 | 390 | 390 | 390 | 390 | 389 | 388 | 387 | 387 | 388 | 388 | 388 |
| 15 | 383 | 383 | 383 | 384 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 384 | 383 | 383 | 384 | 385 | 383 |
| 18 | 378 | 378 | 378 | 378 | 379 | 379 | 379 | 379 | 378 | 380 | 380 | 379 | 377 | 377 | 379 | 379 | 378 |
| 21 | 370 | 371 | 371 | 371 | 372 | 373 | 373 | 372 | 371 | 373 | 373 | 372 | 371 | 371 | 372 | 372 | 371 |
| 24 | 361 | 362 | 363 | 363 | 364 | 363 | 364 | 364 | 364 | 364 | 363 | 362 | 364 | 363 | 362 | 363 | 362 |
| 27 | 353 | 353 | 355 | 355 | 356 | 355 | 354 | 354 | 355 | 355 | 353 | 353 | 356 | 354 | 352 | 352 | 352 |
| 30 | 344 | 343 | 344 | 344 | 346 | 345 | 346 | 344 | 346 | 345 | 345 | 344 | 345 | 343 | 343 | 343 | 341 |
| 33 | 333 | 331 | 333 | 333 | 334 | 333 | 335 | 334 | 335 | 334 | 334 | 333 | 333 | 332 | 333 | 333 | 330 |
| 36 | 320 | 318 | 321 | 321 | 322 | 320 | 321 | 322 | 322 | 322 | 321 | 321 | 321 | 320 | 321 | 320 | 319 |
| 39 | 306 | 306 | 308 | 308 | 309 | 307 | 308 | 309 | 308 | 309 | 308 | 308 | 308 | 307 | 306 | 306 | 305 |
| 42 | 292 | 293 | 295 | 295 | 295 | 294 | 295 | 295 | 294 | 295 | 294 | 294 | 294 | 294 | 292 | 292 | 291 |
| 45 | 278 | 279 | 280 | 279 | 280 | 280 | 281 | 280 | 280 | 279 | 280 | 278 | 279 | 279 | 278 | 277 | 276 |
| 48 | 263 | 265 | 265 | 263 | 264 | 265 | 265 | 263 | 266 | 262 | 265 | 262 | 264 | 263 | 263 | 262 | 260 |
| 51 | 247 | 249 | 249 | 248 | 248 | 249 | 249 | 248 | 251 | 247 | 250 | 248 | 249 | 247 | 248 | 247 | 246 |
| 54 | 230 | 233 | 232 | 231 | 232 | 231 | 232 | 232 | 234 | 232 | 233 | 232 | 232 | 229 | 230 | 232 | 230 |
| 57 | 214 | 214 | 216 | 215 | 215 | 215 | 216 | 215 | 216 | 216 | 216 | 216 | 216 | 214 | 213 | 214 | 214 |
| 60 | 198 | 196 | 198 | 198 | 199 | 199 | 199 | 198 | 198 | 198 | 199 | 198 | 199 | 198 | 196 | 196 | 197 |
| 63 | 183 | 182 | 182 | 182 | 182 | 183 | 182 | 181 | 181 | 182 | 183 | 181 | 182 | 181 | 181 | 181 | 181 |
| 66 | 167 | 166 | 167 | 167 | 167 | 167 | 165 | 165 | 165 | 166 | 167 | 165 | 166 | 166 | 166 | 164 | 164 |
| 69 | 151 | 150 | 150 | 150 | 152 | 151 | 150 | 150 | 150 | 151 | 151 | 149 | 151 | 151 | 148 | 149 | 149 |
| 72 | 136 | 136 | 137 | 135 | 136 | 136 | 136 | 136 | 135 | 136 | 136 | 135 | 137 | 136 | 134 | 135 | 134 |
| 75 | 122 | 122 | 124 | 122 | 123 | 121 | 121 | 122 | 122 | 122 | 121 | 121 | 122 | 121 | 121 | 121 | 121 |
| 78 | 108 | 109 | 110 | 108 | 109 | 108 | 108 | 109 | 108 | 109 | 107 | 109 | 108 | 108 | 109 | 108 | 108 |
| 81 | 94 | 96 | 95 | 94 | 96 | 94 | 94 | 94 | 94 | 94 | 95 | 95 | 96 | 96 | 98 | 98 | 96 |
| 84 | 84 | 83 | 83 | 82 | 84 | 83 | 83 | 83 | 84 | 82 | 83 | 84 | 85 | 83 | 86 | 85 | 86 |
| 87 | 73 | 74 | 72 | 72 | 73 | 71 | 70 | 73 | 72 | 73 | 71 | 73 | 73 | 74 | 74 | 75 | 76 |
| 90 | 63 | 65 | 62 | 64 | 64 | 65 | 63 | 62 | 64 | 63 | 63 | 63 | 64 | 64 | 64 | 66 | 65 |
| 93 | 57 | 57 | 57 | 58 | 58 | 57 | 56 | 56 | 57 | 56 | 57 | 56 | 56 | 58 | 55 | 56 | 56 |
| 96 | 47 | 48 | 48 | 48 | 49 | 48 | 48 | 48 | 49 | 47 | 47 | 46 | 47 | 48 | 45 | 46 | 46 |
| 99 | 39 | 38 | 39 | 38 | 39 | 38 | 39 | 39 | 39 | 39 | 37 | 37 | 37 | 37 | 36 | 36 | 38 |
| 102 | 28 | 28 | 28 | 28 | 28 | 27 | 29 | 28 | 27 | 27 | 28 | 27 | 27 | 27 | 27 | 28 | 29 |
| 105 | 18 | 17 | 18 | 17 | 17 | 18 | 18 | 19 | 17 | 18 | 18 | 18 | 17 | 17 | 17 | 18 | 19 |
| 108 | 9 | 7 | 9 | 8 | 9 | 9 | 9 | 10 | 8 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 10 |
| 111 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |
| 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Table 2b. Luminous intensity values, azimuth 190-350°

Photo 1: Luminaire on goniometer mount

Signature:

_________________________________

Print Name:

D CHAMBERS

_________________________________

Date:

20/11/2014

________________________________

Test Engineer
Duly authorised to sign on behalf of:

Photometric and Optical Testing Services LLP

Checked by:

Signature:

_________________________________

Print Name:

G John

_________________________________

Date: 21/11/2014

________________________________

Technical Director
Duly authorised to sign on behalf of:

Photometric and Optical Testing Services LLP